## BatteryCalculator
[5 empty] | Click here for FireNET Plus -> | [27 empty] | end
Color
The FireNET Battery Calculator Tool is designed to help you choose the batteries for your installation. To use this tool, enter the number of devices that will be attached to your control | [12 empty] | N |  | N, External |  | 24
panel in the yellow cells. Enter the current requirements of any auxiliary devices being powered by the control panel (such as CZMs and ASBs). To use the FireNET outputs for Aux Power, | [12 empty] | Y |  | Y, NAC1 |  | 48
select the desired circuit from the drop down lists. The current requirements will be added to the calculation. Select "N, External" if using an external power supply to provide auxiliary power. | [14 empty] | Y, NAC2 |  | 60
[15 empty] | Y, NAC3 |  | 72
[15 empty] | Y, NAC4 |  | 90
[5 empty] | 24 | Hours | [6 empty] | 35 |  | Y, AUX PWR |  | 24
[5 empty] | 5 | Minutes | [8 empty] | 0
1
FireNET Panel Hardware |  | SLC 1 | SLC 2 | SLC 3 | SLC 4 | Panel Totals | Standby Current | Panel Standby Current |  | Alarm Current | Panel Alarm Current
FN2127 2-Loop Panel | 1 | Ö | Ö |  |  | 1 | 0.35 | 0.35 |  | 0.62 | 0.62 | [5 empty] | 5
FN4127-SLC Loop Expander | 0 |  |  |  |  | 0 | 0.1 | 0 |  | 0.1 | 0 | [5 empty] | 10
FN4127-NIC Network Card | 0 |  |  |  |  | 0 | 0.04 | 0 |  | 0.04 | 0 | [5 empty] | 15
FN-DAC Digital Alarm Communicator | 0 |  |  |  |  | 0 | 0.02 | 0 |  | 0.02 | 0 | [5 empty] | 20
SLC Device Communication Current |  | 0 | 0 | 0 | 0 | 0 | 0.00675 | 0 |  | 0.00675 | 0 | [5 empty] | 30
5 Device Alarm LEDs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.04 | 0 | [5 empty] | 15
[8 empty] | 0.35 | A |  | 0.62 | A
SLC Devices |  | SLC 1 Devices | SLC 2 Devices | SLC 3 Devices | SLC 4 Devices | Device Totals | Device Standby Current | SLC Standby Current |  | Device Alarm Current | SLC Alarm Current | [5 empty] | Device Quantity | Address Count | Sub Address Total
ALG-V Analog Photo Smoke | [5 empty] | 0 | 0.00035 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
ALK-V Analog Photo Smoke | [5 empty] | 0 | 0.00035 | 0 |  | 0.0008 | 0 | [5 empty] | 0 | 1 | 0
ALN-V Analog Photo Smoke | [5 empty] | 0 | 0.00045 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
ACA-V Analog Multi-Sensor | [5 empty] | 0 | 0.00045 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
ACC-V Analog Multi-Sensor | [5 empty] | 0 | 0.00045 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
ACD-V Analog Multi-Criteria Sensor | [5 empty] | 0 | 0.00045 | 0 |  | 0.0072 | 0 | [5 empty] | 0 | 1 | 0
AIE-EA Analog Ion Smoke | [5 empty] | 0 | 0.00035 | 0 |  | 0.00046 | 0 | [5 empty] | 0 | 1 | 0
ATG-EA Analog Heat Sensor | [5 empty] | 0 | 0.00035 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 1 | 0 |  | External | External | NAC 1 | NAC 1 | NAC 2 | NAC 2 | NAC 3 | NAC 3 | NAC 4 | NAC 4 | AUX PWR | AUX PWR
ATJ-EA Analog Heat Sensor | [5 empty] | 0 | 0.00035 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 1 | 0 |  | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr.
Number of Alarm LEDs | [5 empty] | 0 | 0 | 0 |  | 0.008 | 0 | [9 empty] | Standby | Alarm | Standby | Alarm | Standby | Alarm | Standby | Alarm | Standby | Alarm | Standby | Alarm
ASB Analog Sounder Base | [5 empty] | 0 | 0.00011 | 0 |  | 0.00011 | 0 | [5 empty] | 0 | 1 | 0
24V AUX Power Source for ASB |  | N, External | N, External | N, External | N, External |  | 0.00055 |  |  | 0.018 | [9 empty] | asb | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ASBL Analog Low-Frequency Sounder Base | [5 empty] | 0 | 0.00015 | 0 |  | 0.00015 | 0 | [5 empty] | 0 | 1 | 0
24V AUX Power Source for ASBL |  | N, External | N, External | N, External | N, External |  | 0.0023 |  |  | 0.095 | [9 empty] | asbl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DH98-A Analog Duct Detector | [5 empty] | 0 | 0.00035 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 2 | 0
DH98-AR Analog Duct Detector w/Relay | [5 empty] | 0 | 0.00035 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 2 | 0
DH-99-A Analog Duct Detector | [5 empty] | 0 | 0.00035 | 0 |  | 0.0008 | 0 | [5 empty] | 0 | 2 | 0
DH-99-AR Analog Duct Detector w/Relay | [5 empty] | 0 | 0.00035 | 0 |  | 0.0008 | 0 | [5 empty] | 0 | 2 | 0 | DH98-AR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Duct Detector Remote Alarm LEDs | [5 empty] | 0 | 0 |  |  | 0.015 | [9 empty] | DH-99-AR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Duct Detector Remote Power LEDs | [5 empty] | 0 | 0.015 |  |  | 0.015 | [9 empty] | Alarm LED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24V AUX Pwr. Source for DH98-AR & DH-99-AR |  | N, External | N, External | N, External | N, External |  | 0.01 |  |  | 0.06 | [9 empty] | Power LED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRCME-4, P Input Module | [5 empty] | 0 | 0.00055 | 0 |  | 0.00066 | 0 | [5 empty] | 0 | 1 | 0
FRCMA Class A Input Module | [5 empty] | 0 | 0.00063 | 0 |  | 0.0063 | 0 | [5 empty] | 0 | 1 | 0
FRCMA-I Class A Input Module + SCI | [5 empty] | 0 | 0.00063 | 0 |  | 0.0063 | 0 | [5 empty] | 0 | 1 | 0
FRCME-M Input Module | [5 empty] | 0 | 0.00034 | 0 |  | 0.00036 | 0 | [5 empty] | 0 | 1 | 0
DIMM Dual Input Monitor Module | [5 empty] | 0 | 0.0006 | 0 |  | 0.00072 | 0 | [5 empty] | 0 | 3 | 0
AMS Addressable Pull Station | [5 empty] | 0 | 0.00055 | 0 |  | 0.00066 | 0 | [5 empty] | 0 | 1 | 0
CZM Conventional Zone Module | [5 empty] | 0 | 0.000675 | 0 |  | 0.00072 | 0 | [5 empty] | 0 | 1 | 0
24V AUX Power Source for CZM |  | N, External | N, External | N, External | N, External |  | 0.00775 |  |  | 0.06 | [9 empty] | czm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOM Supervised Output Module | [5 empty] | 0 | 0.000154 | 0 |  | 0.000161 | 0 | [5 empty] | 0 | 2 | 0
SOM-A Class A Output Module | [5 empty] | 0 | 0.00042 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 2 | 0 | totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOM-AI Class A Output Module + SCI | [5 empty] | 0 | 0.00042 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 2 | 0
SOM-R Supervised Output Module | [5 empty] | 0 | 0.00015 | 0 |  | 0.00016 | 0 | [5 empty] | 0 | 2 | 0
24V AUX Power for SOMs (see comment)
R2M Dual Relay Module | [5 empty] | 0 | 0.00039 | 0 |  | 0.0004 | 0 | [5 empty] | 0 | 3 | 0
R2ML / R2MH Dual Relay Module | [5 empty] | 0 | 0.00035 | 0 |  | 0.00041 | 0 | [5 empty] | 0 | 3 | 0
R2ML-I / R2MH-I Dual Relay Module + SCI | [5 empty] | 0 | 0.00035 | 0 |  | 0.00041 | 0 | [5 empty] | 0 | 3 | 0
SCI Short Circuit Isolator | [5 empty] | 0 | 0.00027 | 0 |  | 0.00027 | 0
SCI-B6 / SCI-B4 Short Circuit Isolator Base | [5 empty] | 0 | 0.00016 | 0 |  | 0.00016 | 0
SLC Device Count Total - Does not include ASBs, ASBLs, SCIs, or SCI Bases |  | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0
[8 empty] | 0 | A |  | 0 | A
Notification Appliance Circuits |  | NAC 1 | NAC 2 | NAC 3 | NAC 4
NAC Appliance Current per Circuit |  | 0 | 0 | 0 | 0
NAC programmed for Aux Power |  | N | N | N | N
Standby Aux Power from SLC above |  | 0 | 0 | 0 | 0
Alarm Aux Power from SLC above |  | 0 | 0 | 0 | 0
Standby Aux Power from page 2 |  | 0 | 0 | 0 | 0 |  | NAC Standby Current | NAC Alarm Current
Alarm Aux Power from page 2 |  | 0 | 0 | 0 | 0
Total NAC standby current |  | 0 | 0 | 0 | 0
Total NAC alarm current |  | 0 | 0 | 0 | 0 |  | 0 | 0 | A
Auxiliary Power Circuit |  | Aux Pwr
Auxiliary Power Current |  | 0
Constant 24V Power |  | Y
Standby Aux Power from SLC above |  | 0
Alarm Aux Power from SLC above |  | 0
Standby Aux Power from page 2 |  | 0 |  |  |  |  | AUX Power Standby Current | AUX Power Alarm Current
Alarm Aux Power from page 2 |  | 0
Total Aux Power standby current |  | 0
Total Aux Power alarm current |  | 0 |  |  |  |  | 0 | 0 | A
External Power Supply Requirements | [6 empty] | External Standby Current | External Alarm Current
[7 empty] | 0 | 0 | A
If you are using devices that require 24 volt auxiliary power, enter that information in the table below. The total amount of standby and alarm current will be calculated. If you are using
one of the FireNET auxiliary power outputs instead of an external power supply, choose the correct output in the Select AUX PWR Source column.
[13 empty] | External | External | NAC 1 | NAC 1 | NAC 2 | NAC 2 | NAC 3 | NAC 3 | NAC 4 | NAC 4 | AUX PWR | AUX PWR
[13 empty] | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr.
[13 empty] | Stdby | Alarm | Stdby | Alarm | Stdby | Alarm | Stdby | Alarm | Stdby | Alarm | Stdby | Alarm
Auxiliary Power Devices |  | Device Quantity | Standby Current | Alarm Current | Select AUX PWR Source |  |  | Device Standby Current |  |  | Device Alarm Current
Total Standby & Alarm Current for all SOMs |  |  |  |  | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FN-LCD-N Network Annunciator |  |  | 0.15 | 0.27 | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FN-LCD-S Serial Annunciator |  |  | 0.02 | 0.11 | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | A |  | 0 | A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Auxiliary Power Devices on FireNET Panel Circuits |  |  |  |  | Standby |  |  | Alarm
[8 empty] | 0 | A |  | 0 | A
|  |  | Auxiliary Power Devices on External Power Supply |  |  |  |  | Standby |  |  | Alarm
[8 empty] | 0 | A |  | 0 | A
If you are using I/O boards enter that information in the table below. If you are using more than 8 I/O boards, you may enter the information for the additional boards in the Auxiliary
Power Devices table above. If you are using one of the FireNET auxiliary power outputs instead of an external power supply, choose the correct output in the Select AUX PWR
Source column. I/O Board input current current is shown in the table below. I/O Board output current is calculated based on the device(s) connected to the circuit.
[13 empty] | External | External | NAC 1 | NAC 1 | NAC 2 | NAC 2 | NAC 3 | NAC 3 | NAC 4 | NAC 4 | AUX PWR | AUX PWR
[13 empty] | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards | IOboards
I/O Boards | Address | Number of I/O Circuits in Standby | I/O Current in Standby | Number of I/O Circuits in Alarm | I/O Current in Alarm | Select FireNET AUX PWR Source |  | I/O Standby Current |  |  | I/O Alarm Current |  | Stdby Current | Alarm Current | Stdby Current | Alarm Current | Stdby Current | Alarm Current | Stdby Current | Alarm Current | Stdby Current | Alarm Current | Stdby Current | Alarm Current
I/O Board Address #1 | 1 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #2 | 2 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #3 | 3 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #4 | 4 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #5 | 5 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #6 | 6 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #7 | 7 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I/O Board Address #8 | 8 |  |  |  |  | N, External |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inputs |  |  | 0.001 |  | 0.001 |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outputs | [7 empty] | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | I/O Boards powered by FireNET Panel Circuits |  |  |  |  | Standby |  |  | Alarm
[8 empty] | 0 | A |  | 0 | A
|  |  | I/O Boards powered by External Power Supplies |  |  |  |  | Standby |  |  | Alarm
[8 empty] | 0 | A |  | 0 | A
Note: Each I/O Board has 2 banks of 8 I/O channels, channels 1 - 8 and channels 9 - 16. The maximum current output per channel is 0.1A; the maximum current output per bank is 0.5A.
Do not exceed the output capacity of the I/O Board!
Site Information
Total Standby Current Draw = |  | 0.35 | AMPS |  |  | Site Name-
x Standby Time |  | 24 | Hours |  |  | Address-
Standby Amp-Hours Required = |  | 8.4 | AH |  |  | City-
State & ZIP-
Total Alarm Current Draw = |  | 0.62 | AMPS
x Alarm Time |  | 0.083333 | Hours* |  |  | Phone-
Alarm Amp-Hours Required = |  | 0.051667 | AH
Panel Info-
Total AH Required = |  | 8.4517 | AH
x Derating Factor |  | 1.2 | (20%)
Minimum Battery Size: |  | 10.142 | AH
Install Date-
(The FireNET panel can support batteries up to 50 AH. )
* Alarm Time: 0.083=5min, 0.167=10min, 0.250=15min, 0.333=20min, 0.500=30min. | [5 empty] | Misc.-
NOTE: Hochiki hereby disclaims all warranties relating to this software product, whether expressed or implied,
including without limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki
cannot and will not be liable for any incidental, consequential, special, indirect or similar damages for any reason.
It is the responsibility of the user to ascertain the accuracy and the reliability of any and all information generated
or provided by this software.
[10 empty] | Revision | 3.056
Note on B31: These are RAI-LED Remote Alarm Indicators or similar. The indicator is connected between the + side of the SLC and the sensor base. This current is counted as SLC alarm current.
Note on B32: The ASB is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B34: The ASBL is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B37: The DH98-AR is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B39: The DH-99-AR is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B49: The CZM is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B55: The SOMs require auxiliary power. The amount of aux power required by each SOM depends upon the type and number of devices connected to it. Use the Auxiliary Power Devices table below to enter the aux power requirements for all SOM modules.
Note on B73: You must enter the current to be provided by each notification appliance circuit. You may obtain this value by adding together the current of all the devices being powered by the circuit.
Note on B74: If a NAC is being used for Continuous or Resetable Aux Power, set this to Y.
Note on B75: This is the standby Aux Power required by ASBs, CZMs, and duct detectors if one of the NACs was selected as the 24V aux power source for these devices.
Note on B76: This is the alarm Aux Power required by ASBs, CZMs, and duct detectors if one of the NACs was selected as the 24V aux power source for these devices.
Note on B77: These cells will contain the standby Aux Power requirements from the Auxiliary Power Devices list below, if one of the NACs was selected as the 24V aux power source.
Note on B85: Enter the current requirements of all devices connected to the AUX 24V circuit, terminals 18 and 19. The total current must not exceed 0.5 amps.
Note on B87: This is the standby Aux Power required by ASBs, CZMs, and duct detectors if "Y, AUX PWR" was selected as the 24V aux power source.
Note on B88: This is the alarm Aux Power required by ASBs, CZMs, and duct detectors if "Y, AUX PWR" was selected as the 24V aux power source.
Note on B89: This is the Standby Current from the Auxiliary Power Devices list below. This cell will contain the standby current requirements if "Y, AUX PWR" was selected as the aux power source for one or more devices in the Auxiliary Power Devices list.
Note on B90: This is the Alarm Current from the Auxiliary Power Devices list below. This cell will contain the alarm current requirements if "Y, AUX PWR" was selected as the aux power source for one or more devices in the Auxiliary Power Devices list.
Note on B96: This information is provided to help you determine the requirements for an external aux power supply. All devices that have "N, External" as the Aux Power source are included in these totals.
Note on B107: The 24-volt auxiliary power source for ASBs, ASBLs, Duct Detectors, and CZMs must be selected in the SLC Devices table above.
Note on B108: If the SOMs are powered by multiple AUX Power Sources, use additional lines below to enter the standby and alarm current requirements.
Note on D108: Enter the total number of SOMs to be powered by this AUX PWR source
Note on D137: To calculate the standby current for the I/O Board, enter the number of I/O inputs in the Inputs row. Enter the number of I/O outputs in the Outputs row. For example, if you are using 10 inputs, enter 10 in the Inputs row. If you are using I/O board channels as outputs, enter the number of output channels that will require current during standby (non-alarm) conditions. Usually, outputs are only active and require current during alarm, so you may not need to calculate standby time for your I/O board outputs.
Note on E108: Enter the total standby current for all SOMs connected to this AUX Power Source. SOM = 0.000150 A SOM-A / -AI = 0.000050 A Example: If you are using 7 SOMs on this AUX Power Source, enter .00105 here (7 x 0.000150)
Note on E126: "FireNET Panel Circuits" include NAC 1, NAC 2, NAC 3, NAC 4, and AUX Power.
Note on E137: Enter the standby current for the I/O outputs in the Outputs row. The input current is fixed at 0.001 as shown. If you have no I/O board outputs that require current during standby (non-alarm) conditions, you may leave the cell for the output circuits empty.
Note on E163: "FireNET Panel Circuits" include NAC 1, NAC 2, NAC 3, NAC 4, and AUX Power.
Note on F108: Enter the total alarm current for all SOMs connected to this AUX Power Source.
Note on F137: To calculate the alarm current for the I/O Board, enter the number of I/O inputs in the Inputs row. Enter the number of I/O outputs in the Outputs row.
Note on G137: I/O board inputs require 0.001 amps during alarm. I/O board outputs may provide up to 0.1 amp during alarm. Enter the alarm current here. If the alarm current is not the same for all outputs, you may total the current for all circuits and then divide by the number of circuits to obtain the average current; enter this figure in the cell below.
Note on I33: This is the 24V standby current for the ASB. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASB's 24V power.
Note on I35: This is the 24V standby current for the ASBL. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASBL's 24V power.
Note on I40: The duct detector remote alarm LEDs do not require power during standby (non-alarm) conditions.
Note on I41: This is the 24V standby current for the Remote Power LEDs. This is a part of the power required by the DH98-AR/DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on I42: This is the 24V standby current required by the DH98-AR / DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on I50: This is the 24V standby current required by the CZM modules. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the CZM's 24V power.
Note on I77: This is the total standby current for all NACs.
Note on I89: This is the total standby current for the AUX Power circuit (0.5 amps maximum).
Note on I96: This is the total standby current requirement of all devices that have "N, External" selected as the Aux Power Source.
Note on J77: This is the total alarm current for all NACs.
Note on J89: This is the total alarm current for the AUX Power circuit (0.5 amps maximum).
Note on J96: This is the total alarm current requirement of all devices that have "N, External" selected as the Aux Power Source.
Note on L33: This is the 24V alarm current for the ASB. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASB's 24V power.
Note on L35: This is the 24V alarm current for the ASBL. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASBL's 24V power.
Note on L40: This is the 24V current for the Remote Alarm LEDs. This is a part of the power required by the DH98-AR/DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on L41: This is the 24V alarm current for the Remote Power LEDs. This is a part of the power required by the DH98-AR/DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on L42: This is the 24V alarm current required by the DH98-AR / DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on L50: This is the 24V alarm current required by the CZM modules. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the CZM's 24V power.
FireNET Battery Calculator Tool
How much Standby Time (in hours) is required for the installation?
How much Alarm Time* (in minutes) is required for the installation?

## SLC_Wire_Length_Calculator
[7 empty] | Model | Alarm Current |  | SLC1 | SLC2 | SLC3 | SLC4 | [9 empty] | AWG | Resistance | Capacitance | Inductance | Description
[7 empty] | ALN | 0.00054 |  | 0 | 0 | 0 | 0 | //alarm current is taken from the BatteryCalculator sheet automatically. | [7 empty] | SLC1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1
This tool is designed to help you determine the maximum wire length for the Signaling Line Circuit (SLC). The calculator | [6 empty] | ALG | 0.00054 |  | 0 | 0 | 0 | 0 | //alarm current was used as "worst case" even though it is unlikely that all devices will be in alarm at the same time | [7 empty] | SLC2 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1 | <-- these are the linked cells from the dropdown boxes
will collect the number and type of SLC devices from the Battery Calculator tool. You must accurately complete the | [6 empty] | ACA | 0.00054 |  | 0 | 0 | 0 | 0 | [8 empty] | SLC3 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1
FireNET Battery Calculator before using the SLC Wire Length Calculator. | [6 empty] | ALK | 0.0008 |  | 0 | 0 | 0 | 0 | [8 empty] | SLC4 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1
[7 empty] | AIE | 0.00046 |  | 0 | 0 | 0 | 0
Choose a wire from the dropdown list for each of the signaling line circuits in use. If your wire is not listed, click on the | [6 empty] | ATG | 0.0005 |  | 0 | 0 | 0 | 0 | [8 empty] | SLC1 |  | AWG | Resistance | Capacitance | Inductance | Description |  | SLC2 |  | AWG | Resistance | Capacitance | Inductance | Description | SLC3 |  | AWG | Resistance | Capacitance | Inductance | Description | SLC4 |  | AWG | Resistance | Capacitance | Inductance | Description | AWG | Resistance | Capacitance | Inductance | Description
button to enter custom wire information for that circuit, then select "Custom" from the dropdown list. | [6 empty] | ATJ | 0.0005 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 4U1802S3B1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  |  | Paige 4U1802S3B1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded | 18 | 0.00639 | 3.84e-05 | 0.000106 | Solid, FPL, Non-Shielded
[7 empty] | ASB | 0.00011 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454703ARE | 18 | 0.00639 | 38.4 | 0.107 | Solid, FPLR, Non-Shielded |  |  | Paige 454703ARE | 18 | 0.00639 | 38.4 | 0.107 | Solid, FPLR, Non-Shielded |  | Paige 454703ARE | 18 | 0.00639 | 38.4 | 0.107 | Solid, FPLR, Non-Shielded |  | Paige 454703ARE | 18 | 0.00639 | 38.4 | 0.107 | Solid, FPLR, Non-Shielded | 18 | 0.00639 | 3.84e-05 | 0.000107 | Solid, FPLR, Non-Shielded
Do not exceed the maximum wire length as recommended by this calculator. If you require additional information | [6 empty] | DH98 | 0.00054 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 5U1802S3B1 | 18 | 0.0065 | 24 | 0.108 | Solid, FPLP, Non-Shielded |  |  | Paige 5U1802S3B1 | 18 | 0.0065 | 24 | 0.108 | Solid, FPLP, Non-Shielded |  | Paige 5U1802S3B1 | 18 | 0.0065 | 24 | 0.108 | Solid, FPLP, Non-Shielded |  | Paige 5U1802S3B1 | 18 | 0.0065 | 24 | 0.108 | Solid, FPLP, Non-Shielded | 18 | 0.0065 | 2.4e-05 | 0.000108 | Solid, FPLP, Non-Shielded
please contact Hochiki America. | [6 empty] | DH98AR | 0.00054 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454722ARE | 18 | 0.00639 | 64.8 | 0.059 | Solid, FPLR, Shielded |  |  | Paige 454722ARE | 18 | 0.00639 | 64.8 | 0.059 | Solid, FPLR, Shielded |  | Paige 454722ARE | 18 | 0.00639 | 64.8 | 0.059 | Solid, FPLR, Shielded |  | Paige 454722ARE | 18 | 0.00639 | 64.8 | 0.059 | Solid, FPLR, Shielded | 18 | 0.00639 | 6.48e-05 | 5.9e-05 | Solid, FPLR, Shielded
[7 empty] | DH99A | 0.0008 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454717ARER | 18 | 0.00639 | 49.3 | 0.067 | Solid, FPLP, Shielded |  |  | Paige 454717ARER | 18 | 0.00639 | 49.3 | 0.067 | Solid, FPLP, Shielded |  | Paige 454717ARER | 18 | 0.00639 | 49.3 | 0.067 | Solid, FPLP, Shielded |  | Paige 454717ARER | 18 | 0.00639 | 49.3 | 0.067 | Solid, FPLP, Shielded | 18 | 0.00639 | 4.93e-05 | 6.7e-05 | Solid, FPLP, Shielded
[7 empty] | DH99AR | 0.0008 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454731ARE | 16 | 0.00401 | 40.6 | 0.099 | Solid, FPLR, Non-Shielded |  |  | Paige 454731ARE | 16 | 0.00401 | 40.6 | 0.099 | Solid, FPLR, Non-Shielded |  | Paige 454731ARE | 16 | 0.00401 | 40.6 | 0.099 | Solid, FPLR, Non-Shielded |  | Paige 454731ARE | 16 | 0.00401 | 40.6 | 0.099 | Solid, FPLR, Non-Shielded | 16 | 0.00401 | 4.06e-05 | 9.9e-05 | Solid, FPLR, Non-Shielded
[7 empty] | FRCME-4 | 0.00066 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454740ARE | 16 | 0.00419 | 36 | 0.108 | Solid, FPLP, Non-Shielded |  |  | Paige 454740ARE | 16 | 0.00419 | 36 | 0.108 | Solid, FPLP, Non-Shielded |  | Paige 454740ARE | 16 | 0.00419 | 36 | 0.108 | Solid, FPLP, Non-Shielded |  | Paige 454740ARE | 16 | 0.00419 | 36 | 0.108 | Solid, FPLP, Non-Shielded | 16 | 0.00419 | 3.6e-05 | 0.000108 | Solid, FPLP, Non-Shielded
[7 empty] | FRCMA | 0.00063 |  | 0 | 0 | 0 | 0 | //FRCMA/FRCMA-I use standby current in this calculation because alarm current includes LED | [8 empty] | Paige 4S1602S3B1 | 16 | 0.00401 | 72 | 0.052 | Solid, FPL, Shielded |  |  | Paige 4S1602S3B1 | 16 | 0.00401 | 72 | 0.052 | Solid, FPL, Shielded |  | Paige 4S1602S3B1 | 16 | 0.00401 | 72 | 0.052 | Solid, FPL, Shielded |  | Paige 4S1602S3B1 | 16 | 0.00401 | 72 | 0.052 | Solid, FPL, Shielded | 16 | 0.00401 | 7.2e-05 | 5.2e-05 | Solid, FPL, Shielded
Wire Information: | [6 empty] | FRCMA-I | 0.00063 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454736ARE | 16 | 0.0041 | 72 | 0.056 | Solid, FPLR, Shielded |  |  | Paige 454736ARE | 16 | 0.0041 | 72 | 0.056 | Solid, FPLR, Shielded |  | Paige 454736ARE | 16 | 0.0041 | 72 | 0.056 | Solid, FPLR, Shielded |  | Paige 454736ARE | 16 | 0.0041 | 72 | 0.056 | Solid, FPLR, Shielded | 16 | 0.0041 | 7.2e-05 | 5.6e-05 | Solid, FPLR, Shielded
|  | SLC 1 | SLC 2 | SLC 3 | SLC 4 |  | FRCME-M | 0.00036 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454747ARE | 16 | 0.00402 | 52.9 | 0.059 | Solid, FPLP, Shielded |  |  | Paige 454747ARE | 16 | 0.00402 | 52.9 | 0.059 | Solid, FPLP, Shielded |  | Paige 454747ARE | 16 | 0.00402 | 52.9 | 0.059 | Solid, FPLP, Shielded |  | Paige 454747ARE | 16 | 0.00402 | 52.9 | 0.059 | Solid, FPLP, Shielded | 16 | 0.00402 | 5.29e-05 | 5.9e-05 | Solid, FPLP, Shielded
[7 empty] | DIMM | 0.00072 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 4U1402S3B1 | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPL, Non-Shielded |  |  | Paige 4U1402S3B1 | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPL, Non-Shielded |  | Paige 4U1402S3B1 | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPL, Non-Shielded |  | Paige 4U1402S3B1 | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPL, Non-Shielded | 14 | 0.00252 | 4.47e-05 | 0.0001 | Solid, FPL, Non-Shielded
[7 empty] | AMS | 0.00066 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454718ARE | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPLR, Non-Shielded |  |  | Paige 454718ARE | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPLR, Non-Shielded |  | Paige 454718ARE | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPLR, Non-Shielded |  | Paige 454718ARE | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPLR, Non-Shielded | 14 | 0.00252 | 4.47e-05 | 0.0001 | Solid, FPLR, Non-Shielded
| Edit Custom Wire Information: | [5 empty] | CZM | 0.00072 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 5U1402S3R1 | 14 | 0.0025 | 27 | 0.103 | Solid, FPLP, Non-Shielded |  |  | Paige 5U1402S3R1 | 14 | 0.0025 | 27 | 0.103 | Solid, FPLP, Non-Shielded |  | Paige 5U1402S3R1 | 14 | 0.0025 | 27 | 0.103 | Solid, FPLP, Non-Shielded |  | Paige 5U1402S3R1 | 14 | 0.0025 | 27 | 0.103 | Solid, FPLP, Non-Shielded | 14 | 0.0025 | 2.7e-05 | 0.000103 | Solid, FPLP, Non-Shielded
[7 empty] | SOM | 0.000161 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 4S1402S3R1 | 14 | 0.00252 | 58 | 0.052 | Solid, FPL, Shielded |  |  | Paige 4S1402S3R1 | 14 | 0.00252 | 58 | 0.052 | Solid, FPL, Shielded |  | Paige 4S1402S3R1 | 14 | 0.00252 | 58 | 0.052 | Solid, FPL, Shielded |  | Paige 4S1402S3R1 | 14 | 0.00252 | 58 | 0.052 | Solid, FPL, Shielded | 14 | 0.00252 | 5.8e-05 | 5.2e-05 | Solid, FPL, Shielded
| Size: | 18 | 18 | 18 | 18 |  | SOM-A | 0.0005 |  | 0 | 0 | 0 | 0 | [9 empty] | Paige 454726ARE | 14 | 0.00252 | 58 | 0.052 | Solid, FPLR, Shielded |  |  | Paige 454726ARE | 14 | 0.00252 | 58 | 0.052 | Solid, FPLR, Shielded |  | Paige 454726ARE | 14 | 0.00252 | 58 | 0.052 | Solid, FPLR, Shielded |  | Paige 454726ARE | 14 | 0.00252 | 58 | 0.052 | Solid, FPLR, Shielded | 14 | 0.00252 | 5.8e-05 | 5.2e-05 | Solid, FPLR, Shielded
| Resistance (Ω/ft): | 0.00639 | 0.00639 | 0.00639 | 0.00639 |  | SOM-AI | 0.0005 |  | 0 | 0 | 0 | 0 |  | SCI Calculation | R | SLC1 | SLC2 | SLC3 | SLC4 |  |  | Paige 454727ARE | 14 | 0.00253 | 67 | 0.053 | Solid, FPLP, Shielded |  |  | Paige 454727ARE | 14 | 0.00253 | 67 | 0.053 | Solid, FPLP, Shielded |  | Paige 454727ARE | 14 | 0.00253 | 67 | 0.053 | Solid, FPLP, Shielded |  | Paige 454727ARE | 14 | 0.00253 | 67 | 0.053 | Solid, FPLP, Shielded | 14 | 0.00253 | 6.7e-05 | 5.3e-05 | Solid, FPLP, Shielded
| Capacitance (pF/ft): | 38.4 | 38.4 | 38.4 | 38.4 |  | SOM-R | 0.00016 |  | 0 | 0 | 0 | 0 |  | SCI Bases | 3e-05 | 0 | 0 | 0 | 0 | (row 59) |  | Custom | 16 | 0.0025 | 49.3 | 0.066 | Enter Description... |  |  | Custom | 16 | 0.0025 | 49.3 | 0.066 | Enter Description... |  | Custom | 16 | 0.0025 | 49.3 | 0.066 | Enter Description... |  | Custom | 16 | 0.015 | 49.3 | 0.07 | Enter Description... | 18 | 0.00222 | 3.3e-05 | 4.4e-05 | Enter Description...
| Inductance (µH/ft): | 0.106 | 0.106 | 0.106 | 0.106 |  | R2M | 0.0004 |  | 0 | 0 | 0 | 0 |  | FRCMA-I | 3e-05 | 0 | 0 | 0 | 0 | (row 44)
|  | Solid, FPL, Non-Shielded | Solid, FPL, Non-Shielded | Solid, FPL, Non-Shielded | Solid, FPL, Non-Shielded |  | R2ML/H | 0.00041 |  | 0 | 0 | 0 | 0 |  | SOM-AI | 3e-05 | 0 | 0 | 0 | 0 | (row 52)
[7 empty] | R2ML/H-I | 0.00041 |  | 0 | 0 | 0 | 0 |  | R2M-I | 3e-05 | 0 | 0 | 0 | 0 | (row 57)
[7 empty] | SCI | 0.00027 |  | 0 | 0 | 0 | 0 |  | SCI | 5e-05 | 0 | 0 | 0 | 0 | (row 58)
|  | SLC 1 | SLC 2 | SLC 3 | SLC 4 |  | SCI_Base | 0.00016 |  | 0 | 0 | 0 | 0
| Number of Devices | 0 | 0 | 0 | 0 |  | ACC | 0.00054 |  | 0 | 0 | 0 | 0
[7 empty] | ASBL | 0.00015 |  | 0 | 0 | 0 | 0
| MAX SLC Wire Length | 0 | 0 | 0 | 0 | feet
[16 empty] | SCI Rtotal | 0 | 0 | 0 | 0
| Overall Length Limited by: | [7 empty] | Sub -> | 0 | 0 | 0 | 0
// If any of the row numbers are changed on battery calculator sheet this table must be updated.
[7 empty] | 5 LEDs | 0.04 |  | 0 | 0 | 0 | 0
[7 empty] | Comms | 0.007 |  | 0 | 0 | 0 | 0
[9 empty] | Total -> | 0 | 0 | 0 | 0 | //worst-case maximum current for each SLC
[9 empty] | Rtotal | 0 | 0 | 0 | 0 | //this is the total maximum resistance for the SLC based on V/I
//V = 6 volt drop maximum for FireNET and FireNET Plus panels
For information on how to measure the total SLC wire length, click here: | [8 empty] | SCI Rtotal | 0 | 0 | 0 | 0 | //this is the total resistance of SCI devices on the circuit.
[9 empty] | Wire Rmax | 0 | 0 | 0 | 0 | //adjusted total resistance after subtracting SCIs
|  | Paige Wire nominal OD (for conduit fill calculations) | [6 empty] | Adjusted Rmax | 0 | 0 | 0 | 0 | //since the DCP spec states "less than 50 ohms" I set this to be 49.9 ohms maximum
|  | 18AWG | 16AWG | 14AWG |  |  |  |  | CableResistance | 0.00639 | 0.00639 | 0.00639 | 0.00639
|  | 4U1802S3B1 - 0.161" | 454731ARE - 0.180" | 4U1402S3B1 - 0.220" |  |  |  |  | MaxWire based on Resistance | 0 | 0 | 0 | 0 | //this is the maximum wire length based on the resistance, Rmax divided by the cable resistance per foot
|  | 454703ARE - 0.160" | 454740ARE - 0.170" | 454718ARE - 0.220"
|  | 5U1802S3B1 - 0.134" | 4S1602S3B1 - 0.161" | 5U1402S3R1 - 0.206" |  |  |  |  | CableCapacitance | 38.4 | 38.4 | 38.4 | 38.4
|  | 454722ARE - 0.161" | 454736ARE - 0.160" | 4S1402S3R1 - 0.218" |  |  |  |  | MaxWire based on Capacitance | 25781.25 | 25781.25 | 25781.25 | 25781.25 | //max capacitance = .99µf total (less than 1µf). This is used to determine max wire length based on capacitance. Note that pf is used for the calculation (.99µf = 990000pf)
|  | 454717ARER - 0.145" | 454747ARE - 0.170" | 454726ARE - 0.210"
|  |  |  | 454727ARE - 0.200" |  |  |  |  | CableInductance | 0.106 | 0.106 | 0.106 | 0.106
[9 empty] | MaxWire based on Inductance | 9339.6226 | 9339.6226 | 9339.6226 | 9339.6226 | //max inductance = .99mH total (less than 1mH). This is used to determine max wire length based on inductance. Note that µH is used for the calculation (.99mH - 990µH)
NOTE: Hochiki hereby disclaims all warranties relating to this software product, whether expressed or implied, including without | [8 empty] | Maximum SLC Length | 0 | 0 | 0 | 0 | //determines and displays the max SLC length based on limiting factor (resistance, inductance, capacitance)
limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki cannot and will not be liable for any | [9 empty] | 0 | 0 | 0 | 0 | //limits max SLC length to preset value
incidental, consequential, special, indirect or similar damages for any reason. It is the responsibility of the user to ascertain the accuracy
and the reliability if any and all information generated or provided by this software. | [8 empty] | SLC Preset Length Value (ft.) | 10000 |  |  |  | //this is the preset SLC length. This is the maximum distance that the calculator will display to the user. Change the number in this cell to adjust the maximum distance.
Revision | 3.056 | [12 empty] | //Operation of wire selection tool
//drop down boxes are ActiveX combo boxes. The range displayed in the list is set in the properties for the controls.
//The linked cells for the combo boxes are at AM3:AM6.
//AF2:AJ5 uses VLOOKUP to find the correct information for the wire that has been selected.
//The buttons call a user form. When the user form is closed, the data entered is written to the "Custom" row in each SLC's data table
// The data in AF2:AJ5 is copied to the cells on the part of the form that is visible to the user
//To update the wire information:
//the information in the tables must be updated for all 4 SLCs
[10 empty] | Class B |  |  |  | // the range may need to be changed for each combo box (if the number of table entries have changed)
[10 empty] | Class B with T-taps |  |  |  | //the range may need to be changed for the VLOOKUP formulas (if the number of table entries have changed)
[10 empty] | Class A |  |  |  | //If the location of the "Custom" wire cells has changed, the VB code must be changed for the cmdAdd_click events
//(this event writes the user-entered information to specific cells on the sheet. cmdSaveAll_click on user form 1 must be changed too)
Note on C31: All Addressable SLC Devices. NOTE that this number may exceed 127 if ASB / ASBLs are used.
The maximum values for the SLC are:
Resistance - less than 50 ohms
Capacitance - less than 1 µF
Inductance - less than 1 mH
Description:
FireNET SLC Wire Length Calculator

## FNP_BatteryCalculator (hidden)
[6 empty] | Click here for FireNET -> | [8 empty] | BEWARE! Adding rows or colums may cause the functions to operate incorrectly or not at all. | [15 empty] | end
[12 empty] | Color |  | N |  | N, External |  | 24
[14 empty] | Y |  | Y, NAC1 |  | 48
[16 empty] | Y, NAC2 |  | 60
[16 empty] | Y, 24V OUT |  | 72
[16 empty] | Y, AUX 24V |  | 90
[6 empty] | 24 | Hours | [6 empty] | 35 |  |  |  | 24
[6 empty] | 5 | Minutes | [8 empty] | 0
1
| FireNET Plus Panel Hardware |  | SLC 1 | SLC 2 | Panel Totals | Standby Current | Panel Standby Current |  | Alarm Current | Panel Alarm Current
| FNP-1127 1-Loop Panel | 1 | Ö |  | 1 | 0.2 | 0.2 |  | 0.25 | 0.25 | [7 empty] | 5
| FNP-1127-SLC Loop Expander | 1 |  | Ö | 1 | 0.075 | 0.075 |  | 0.075 | 0.075 | [7 empty] | 10
| FN4127-NIC Network Card | 0 |  |  | 0 | 0.04 | 0 |  | 0.04 | 0 | [7 empty] | 15
| Integrated DACT Option | 0 |  |  | 0 | 0.025 | 0 |  | 0.025 | 0 | [7 empty] | 20
| SLC Device Communication Current |  | 0 | 0 | 0 | 0.00675 | 0 |  | 0.00675 | 0 | [7 empty] | 30
| 5 Device Alarm LEDs |  | 0 | 0 | 0 | 0 | 0 |  | 0.04 | 0 | [7 empty] | 15
[7 empty] | 0.275 | A |  | 0.325 | A
| SLC Devices |  | SLC 1 Devices | SLC 2 Devices | Device Total | Device Standby Current | SLC Standby Current |  | Device Alarm Current | SLC Alarm Current | [5 empty] | Device Quantity | Address Count | Sub Address Total
| ALG-V Analog Photo Smoke |  |  |  | 0 | 0.00039 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
| ALK-V Analog Photo Smoke |  |  |  | 0 | 0.00039 | 0 |  | 0.0008 | 0 | [5 empty] | 0 | 1 | 0
| ALN-V Analog Photo Smoke |  |  |  | 0 | 0.00045 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
| ACA-V Analog Multi-Sensor |  |  |  | 0 | 0.00045 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
| ACC-V Analog Multi-Sensor |  |  |  | 0 | 0.00045 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 1 | 0
| ACD-V Analog Multi-Criteria Sensor |  |  |  | 0 | 0.00045 | 0 |  | 0.0072 | 0 | [5 empty] | 0 | 1 | 0
| AIE-EA Analog Ion Smoke |  |  |  | 0 | 0.00035 | 0 |  | 0.00046 | 0 | [5 empty] | 0 | 1 | 0
| ATG-EA Analog Heat Sensor |  |  |  | 0 | 0.00035 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 1 | 0 |  | External | External | NAC 1 | NAC 1 | NAC 2 | NAC 2 | 24V OUT | 24V OUT | AUX 24V | AUX 24V
| ATJ-EA Analog Heat Sensor |  |  |  | 0 | 0.00035 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 1 | 0 |  | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr.
| Number of Alarm LEDs |  |  |  | 0 | 0 | 0 |  | 0.008 | 0 | [9 empty] | Standby | Alarm | Standby | Alarm | Standby | Alarm | Standby | Alarm | Standby | Alarm
| ASB Analog Sounder Base |  |  |  | 0 | 0.00011 | 0 |  | 0.00011 | 0 | [5 empty] | 0 | 1 | 0
| 24V AUX Power Source for ASB |  | N, External | N, External |  | 0.00055 |  |  | 0.018 | [9 empty] | asb | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ASBL Analog Low-Frequency Sounder Base |  |  |  | 0 | 0.00015 | 0 |  | 0.00015 | 0 | [5 empty] | 0 | 1 | 0
| 24V AUX Power Source for ASBL |  | N, External | N, External |  | 0.0023 |  |  | 0.095 | [9 empty] | asbl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DH98-A Analog Duct Detector |  |  |  | 0 | 0.00039 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 2 | 0
| DH98-AR Analog Duct Detector w/Relay |  |  |  | 0 | 0.00039 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 2 | 0 | dh98ar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| DH-99-A Analog Duct Detector |  |  |  | 0 | 0.00039 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 2 | 0
| DH-99-AR Analog Duct Detector w/Relay |  |  |  | 0 | 0.00039 | 0 |  | 0.00054 | 0 | [5 empty] | 0 | 2 | 0 | dh99ar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Duct Detector Remote Alarm LEDs |  |  |  | 0 | 0 |  |  | 0.015 | [9 empty] | remote alarm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Duct Detector Remote Power LEDs |  |  |  | 0 | 0.015 |  |  | 0.015 | [9 empty] | remote power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 24V AUX Pwr. Source for DH98-AR & DH-99-AR |  | N, External | N, External |  | 0.01 |  |  | 0.06
| FRCME-4, P Input Module |  |  |  | 0 | 0.00055 | 0 |  | 0.00066 | 0 | [5 empty] | 0 | 1 | 0
| FRCMA Class A Input Module |  |  |  | 0 | 0.00063 | 0 |  | 0.0063 | 0 | [5 empty] | 0 | 1 | 0
| FRCMA-I Class A Input Module + SCI |  |  |  | 0 | 0.00063 | 0 |  | 0.0063 | 0 | [5 empty] | 0 | 1 | 0
| FRCME-M Input Module |  |  |  | 0 | 0.00034 | 0 |  | 0.00036 | 0 | [5 empty] | 0 | 1 | 0
| DIMM Dual Input Monitor Module |  |  |  | 0 | 0.0006 | 0 |  | 0.00072 | 0 | [5 empty] | 0 | 3 | 0
| AMS Addressable Pull Station |  |  |  | 0 | 0.00055 | 0 |  | 0.00066 | 0 | [5 empty] | 0 | 1 | 0
| CZM Conventional Zone Module |  |  |  | 0 | 0.000675 | 0 |  | 0.00072 | 0 | [5 empty] | 0 | 1 | 0
| 24V AUX Power Source for CZM |  | N, External | N, External |  | 0.00775 |  |  | 0.06 | [9 empty] | czm | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SOM Supervised Output Module |  |  |  | 0 | 0.000154 | 0 |  | 0.000161 | 0 | [5 empty] | 0 | 2 | 0
| SOM-A Class A Output Module |  |  |  | 0 | 0.00042 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 2 | 0 | total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SOM-AI Class A Output Module + SCI |  |  |  | 0 | 0.00042 | 0 |  | 0.0005 | 0 | [5 empty] | 0 | 2 | 0
| SOM-R Supervised Output Module |  |  |  | 0 | 0.00015 | 0 |  | 0.00016 | 0 | [5 empty] | 0 | 2 | 0
24V AUX Power for SOMs (see note)
| R2M Dual Relay Module |  |  |  | 0 | 0.00039 | 0 |  | 0.0004 | 0 | [5 empty] | 0 | 3 | 0
| R2ML / R2MH Dual Relay Module |  |  |  | 0 | 0.00035 | 0 |  | 0.000405 | 0 | [5 empty] | 0 | 3 | 0
| R2ML-I, R2MH-I Dual Relay Module + SCI |  |  |  | 0 | 0.00035 | 0 |  | 0.000405 | 0 | [5 empty] | 0 | 3 | 0
| SCI Short Circuit Isolator |  |  |  | 0 | 0.00027 | 0 |  | 0.00027 | 0 | [6 empty] | 0 | 0
| SCI-B6 / SCI-B4 Short Circuit Isolator Base |  |  |  | 0 | 0.00016 | 0 |  | 0.00016 | 0
| SLC Device Count Total - Does not include ASBs, SCIs, or SCI Bases |  | 0 | 0 | 0 | [12 empty] | 0
[7 empty] | 0 | A |  | 0 | A
| Notification Appliance Circuits |  | NAC 1 | NAC 2
| NAC Appliance Current per Circuit |  | 0 | 0
| NAC programmed for Aux Power |  | N | N
| Standby Aux Power from SLC above |  | 0 | 0
| Alarm Aux Power from SLC above |  | 0 | 0
| Standby Aux Power from page 2 |  | 0 | 0 |  |  | NAC Standby Total |  | NAC Alarm Total
| Alarm Aux Power from page 2 |  | 0 | 0
| Total NAC standby current |  | 0 | 0
| Total NAC alarm current |  | 0 | 0 |  |  | 0 | A | 0 | A
| Auxiliary Power Circuits |  | 24V OUT | AUX 24V
| Auxiliary Power Current |  | 0 | 0
| Constant 24V Power |  | Y | Y
| Standby Aux Power from SLC above |  | 0 | 0
| Alarm Aux Power from SLC above |  | 0 | 0
| Standby Aux Power from page 2 |  | 0 | 0 |  |  | AUX Standby Total |  | AUX Alarm Total
| Alarm Aux Power from page 2 |  | 0 | 0
| Total Aux Power standby current |  | 0 | 0
| Total Aux Power alarm current |  | 0 | 0 |  |  | 0 | A | 0 | A
| External Power Supply Requirements | [5 empty] | External Standby Total |  | External Alarm Total
[7 empty] | 0 | A | 0 | A
If you are using devices that require 24 volt auxiliary power, enter that information in the table below. The total amount of standby and alarm current required will be calculated. If you
| are using one of the FireNET Plus auxiliary power outputs instead of an external power supply, choose the correct output in the Select AUX PWR Source column. | [12 empty] | External | External | NAC 1 | NAC 1 | NAC 2 | NAC 2 |  |  | 24V OUT | 24V OUT | AUX 24V | AUX 24V
| Auxiliary Power Devices |  | Device Quantity | Standby Current | Alarm Current | Select AUX PWR Source |  |  | Device Standby Current |  |  | Device Alarm Current |  | Stdby Current | Alarm Current | Stdby Current | Alarm Current | Stdby Current | Alarm Current |  |  | Stdby Current | Alarm Current | Stdby Current | Alarm Current
| # of SOMs X Alarm Current per SOM |  |  |  |  | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| FN-LCD-N Network Annunciator |  |  | 0.15 | 0.27 | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| FN-LCD-S Serial Annunciator |  |  | 0.02 | 0.11 | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[6 empty] | N, External |  |  | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[9 empty] | 0 | A |  | 0 | A | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  |  | A
|  |  |  | Auxiliary Power Devices on FireNET Plus Circuits |  |  |  |  | Standby |  |  | Alarm
[9 empty] | 0 | A |  | 0 | A | [16 empty] | A
|  |  |  | Auxiliary Power Devices on External Power Supply |  |  |  |  | Standby |  |  | Alarm
[9 empty] | 0 | A |  | 0 | A | [16 empty] | A
[14 empty] | External | External | NAC 1 | NAC 1 | NAC 2 | NAC 2 |  |  | 24V OUT | 24V OUT | AUX 24V | AUX 24V
[14 empty] | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. |  |  | Aux.Pwr. | Aux.Pwr. | Aux.Pwr. | Aux.Pwr.
| I/O & LED Boards | Address | Number of I/O Circuits in Standby | Standby Current | Number of I/O Circuits in Alarm | Alarm Current | Select FireNET Plus AUX PWR Source |  | I/O Standby Current |  |  | I/O Alarm Current |  | Stdby Current | Alarm Current | Stdby Current | Alarm Current | Stdby Current | Alarm Current |  |  | Stdby Current | Alarm Current | Stdby Current | Alarm Current
1 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
2 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
6 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
7 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8 | None |  |  | 0.000 |  | 0.000 | N, External |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Inputs |  |  | 0.001 |  | 0.001 |  |  | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Outputs | [7 empty] | 0.000 |  |  | 0.000 |  | 0.000 | 0.000 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[14 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
|  |  |  | I/O Boards powered by FireNET Plus Circuits |  |  |  |  | Standby |  |  | Alarm
[9 empty] | 0 | A |  | 0 | A | [16 empty] | A
|  |  |  | I/O Boards powered by External Power Supplies |  |  |  |  | Standby |  |  | Alarm
[9 empty] | 0 | A |  | 0 | A | [16 empty] | A
| Note: Each I/O Board has 2 banks of 8 I/O channels; channels 1 - 8 and 9 - 16. The maximum current output per channel is 0.1A; the maximum current output per bank is 0.5A. | [13 empty] | None |  |  | standby | alarm
| Do not exceed the output capacity of the I/O Board! | [13 empty] | I/O Board (FN-4127-IO) |  |  | 0.008 | 0.008
[10 empty] | Site Information |  |  |  |  | LED Driver Board, 8 LEDs (FNP-LED) |  |  | 0.013 | 0.045 |  | The section to the left is for the I/O Board table.
| Total Standby Current Draw = |  | 0.275 | AMPS |  |  | Site Name- | [7 empty] | LED Expansion Board, 16 LEDs (FNP-LED) |  |  | 0.013 | 0.045 |  | When a selection is made from a combo box, that entry is put into the list on the left.
| x Standby Time |  | 24 | Hours |  |  | Address- | [13 empty] | The DONE button on the form hides or unhides rows based on the setting of the combo box values
| Standby Amp-Hours Required = |  | 6.6 | AH |  |  | City- | [7 empty] | None | [5 empty] | If rows are added or deleted, all of this will stop working and must be adjusted to account for the increase or decrease of rows.
[7 empty] | State & ZIP- | [7 empty] | None | [5 empty] | To improve this next time, put all of this above where rows will be added. This will prevent such changes from occurring.
| Total Alarm Current Draw = |  | 0.325 | AMPS | [10 empty] | None | [5 empty] | And will save you a lot of pain and suffering as well. :-(
| x Alarm Time |  | 0.083333 | Hours* |  |  | Phone- | [7 empty] | None
| Alarm Amp-Hours Required = |  | 0.027083 | AH | [10 empty] | None
[7 empty] | Panel Info- | [7 empty] | None
| Total AH Required = |  | 6.6271 | AH | [10 empty] | None
| x Derating Factor |  | 1.2 | (20%) | [10 empty] | None
| Minimum Battery Size: |  | 7.9525 | AH
Install Date-
(The FireNET Plus panel can support batteries up to 60 AH. )
| * Alarm Time: 0.083=5min, 0.167=10min, 0.250=15min, 0.333=20min, 0.500=30min. | [5 empty] | Misc.-
[10 empty] | Revision | 3.056
Note on B31: These are RAI-LED Remote Alarm Indicators or similar. The indicator is connected between the + side of the SLC and the sensor base. This current is counted as SLC alarm current.
Note on B32: The ASB is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B34: The ASBL is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B37: The DH98-AR is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B39: The DH-99-AR is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B49: The CZM is a 4-wire device. It requires: 1) a connection to the SLC; 2) 24VDC power. Select the 24V power source using the dropdown boxes to the right.
Note on B55: The SOMs require auxiliary power. The amount of aux power required by each SOM depends upon the type and number of devices connected to it. Use the Auxiliary Power Devices table below to enter the aux power requirements for all SOM modules.
Note on B73: You must enter the current to be provided by each notification appliance circuit. You may obtain this value by adding together the current of all the devices being powered by the circuit.
Note on B74: If a NAC is being used for Continuous or Resetable Aux Power, set this to Y.
Note on B75: This is the standby Aux Power required by ASBs, CZMs, and duct detectors if one of the NACs was selected as the 24V aux power source.
Note on B76: This is the alarm Aux Power required by ASBs, CZMs, and duct detectors if one of the NACs was selected as the 24V aux power source.
Note on B77: This is the Standby Current from the Auxiliary Power Devices list below. These cells will contain the standby Aux Power requirements if one of the NACs was selected as the 24V aux power source.
Note on B78: This is the Alarm Current from the Auxiliary Power Devices list below. These cells will contain the alarm Aux Power requirements if one of the NACs was selected as the 24V aux power source.
Note on B85: Enter the current requirements of all devices connected to the 24V OUT and AUX 24V circuits. The total current must not exceed 0.36 amps per circuit.
Note on B87: This is the standby Aux Power required by ASBs, CZMs, and duct detectors if "Y, 24V OUT" or "Y, AUX 24V" was selected as the 24V aux power source.
Note on B88: This is the alarm Aux Power required by ASBs, CZMs, and duct detectors if "Y, 24V OUT" or "Y, AUX 24V" was selected as the 24V aux power source.
Note on B89: This is the Standby Current from the Auxiliary Power Devices list below. These cells will contain the standby current requirements if "Y, 24V OUT" or "Y, AUX 24V" was selected as the aux power source for one or more devices in the Auxiliary Power Devices list.
Note on B90: This is the Alarm Current from the Auxiliary Power Devices list below. These cells will contain the alarm current requirements if "Y, 24V OUT" or "Y, AUX 24V" was selected as the aux power source for one or more devices in the Auxiliary Power Devices list.
Note on B100: This information is provided to help you determine the requirements for an external aux power supply. All devices that have "N, External" as the Aux Power source are included in these totals.
Note on B111: The 24-volt auxiliary power source for ASBs, Duct Detectors, and CZMs must be selected in the SLC Devices table above.
Note on B112: If SOMs are powered by multiple AUX Power Sources, use additional lines below to enter the standby and alarm current requirements.
Note on C141: You may enter the address of the module in this column, up to 8 modules.
Note on D112: Enter the total number of SOMs to be powered by this AUX PWR source
Note on D141: Only the I/O Board requires this entry. To calculate the standby current for the I/O Board, enter the number of I/O inputs in the Inputs row. Enter the number of I/O outputs in the Outputs row. For example, if you are using 10 inputs, enter 10 in the Inputs row. If you are using I/O board channels as outputs, enter the number of output channels that will require current during standby (non-alarm) conditions. Usually, outputs are only active and require current during alarm, so you may not need to calculate standby time for your I/O board outputs.
Note on E112: Enter the total standby current for all SOMs connected to this AUX Power Source. SOM = 0.000150 A SOM-A / -AI = 0.000050 A Example: If you are using 7 SOMs on this AUX Power Source, enter .00105 here (7 x 0.000150)
Note on E130: FireNET Plus Circuits include NAC 1, NAC 2, 24V OUT, and AUX 24V.
Note on E141: Each module requires standby current. This is added automatically based on the type of device selected. If you are using I/O Boards, enter the standby current for the I/O outputs in the Outputs row. The input current is fixed at 0.001 as shown. If you don't have any I/O board outputs that require current during standby (non-alarm) conditions, you may leave the cell for the output circuits empty.
Note on E167: FireNET Plus Circuits include NAC 1, NAC 2, 24V OUT, and AUX 24V.
Note on F112: Enter the total alarm current for all SOMs connected to this AUX Power Source.
Note on F141: Only the I/O Board requires this entry. To calculate the alarm current for the I/O Board, enter the number of I/O inputs in the Inputs row. Enter the number of I/O outputs in the Outputs row.
Note on G33: This is the 24V standby current for the ASB. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASB's 24V power.
Note on G35: This is the 24V standby current for the ASBL. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASBL's 24V power.
Note on G40: The duct detector remote alarm LEDs do not require power during standby (non-alarm) conditions.
Note on G41: This is the 24V standby current for the Remote Power LEDs. This is a part of the power required by the DH98-AR/DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on G42: This is the 24V standby current required by the DH98-AR / DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on G50: This is the 24V standby current required by the CZM modules. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the CZM's 24V power.
Note on G141: Each module requires alarm current. This is added automatically based on the type of device selected. I/O board inputs require 0.001 amps during alarm. I/O board outputs may provide up to 0.1 amp during alarm. Enter the alarm current here. If the alarm current is not the same for all outputs, you may total the current for all circuits and then divide by the number of circuits to obtain the average current; enter this figure in the cell below.
Note on H77: This is the total standby current for all NACs.
Note on H89: This is the total standby current for the 24V OUT and AUX 24V circuits.
Note on J33: This is the 24V alarm current for the ASB. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASB's 24V power.
Note on J35: This is the 24V alarm current for the ASBL. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the ASBL's 24V power.
Note on J40: This is the 24V current for the Remote Alarm LEDs. This is a part of the power required by the DH98-AR/DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on J41: This is the 24V alarm current for the Remote Power LEDs. This is a part of the power required by the DH98-AR/DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on J42: This is the 24V alarm current required by the DH98-AR / DH-99-AR duct detectors. Use the dropdown boxes to the left to select the correct source for the duct detector's 24V power.
Note on J50: This is the 24V alarm current required by the CZM modules. This power is not provided by the SLC. Use the dropdown boxes to the left to select the correct source for the CZM's 24V power.
Note on J77: This is the total alarm current for all NACs.
Note on J89: This is the total alarm current for the 24V OUT and AUX 24V circuits.
The FireNET Plus Battery Calculator Tool is designed to help you determine the batteries needed for your installation. To use this tool, enter the number of devices that will be
attached to your control panel in the yellow cells. Enter the current requirements of any auxiliary devices being powered by the control panel (such as CZMs and ASBs). To use the FireNET Plus outputs for your Auxiliary Power, select the desired circuit from the drop down lists. The current requirements will be added to the calculation. Select "N, External" if using
an external power supply to provide auxiliary power.
How much Standby Time (in hours) is required for the installation?
How much Alarm Time* (in minutes) is required for the installation?
FireNET Plus Battery Calculator Tool
NOTE: Hochiki hereby disclaims all warranties relating to this software product, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki cannot and will not be liable for any incidental, consequential, special, indirect or similar damages for any reason. It is the responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software.
If you are using I/O or LED boards, click on the Select button to enter the information. If you are using more than 8 boards, you may enter the information for the additional boards in the Auxiliary Power Devices table above. If you are using one of the FireNET Plus auxiliary power outputs instead of an external power supply, choose the correct output in the Select AUX PWR Source column. If you are using I/O Boards you must enter the number of inputs in use and the number of outputs; you must also enter the output current per channel. The current requirements for the board itself are automatically calculated.

## FNP_SLC_Wire_Length_Calculator (hidden)
[5 empty] | Model | Alarm Current |  | SLC1 | SLC2 | [7 empty] | size | Resistance | Capacitance | Inductance | Description
[5 empty] | ALN | 0.00054 |  | 0 | 0 | //alarm current is taken from the BatteryCalculator sheet automatically. | [5 empty] | SLC1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1
[5 empty] | ALG | 0.00054 |  | 0 | 0 | //alarm current was used as "worst case" even though it is unlikely that all devices will be in alarm at the same time | [5 empty] | SLC2 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  | Paige 4U1802S3B1
This tool is designed to help you determine the maximum wire length for the Signaling Line Circuit (SLC). The |  |  |  |  | ACA | 0.00054 |  | 0 | 0
calculator will collect the number and type of SLC devices from the Battery Calculator tool. You must accurately |  |  |  |  | ALK | 0.0008 |  | 0 | 0
complete the FireNET Plus Battery Calculator before using the SLC Wire Length Calculator. |  |  |  |  | AIE | 0.00046 |  | 0 | 0
[5 empty] | ATG | 0.0005 |  | 0 | 0 | [6 empty] | SLC1 |  | size | Resistance | Capacitance | Inductance | Description |  | SLC2 |  | size | Resistance | Capacitance | Inductance | Description | Description
Choose a wire from the dropdown list for each of the signaling line circuits in use. If your wire is not listed, click on the |  |  |  |  | ATJ | 0.0005 |  | 0 | 0 | [7 empty] | Paige 4U1802S3B1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded |  |  | Paige 4U1802S3B1 | 18 | 0.00639 | 38.4 | 0.106 | Solid, FPL, Non-Shielded | Solid, FPL, Non-Shielded
button to enter custom wire information for that circuit, then select "Custom" from the dropdown list. |  |  |  |  | ASB | 0.00011 |  | 0 | 0 | [7 empty] | Paige 454703ARE | 18 | 0.00639 | 38.4 | 0.107 | Solid, FPLR, Non-Shielded |  |  | Paige 454703ARE | 18 | 0.00639 | 38.4 | 0.107 | Solid, FPLR, Non-Shielded | Solid, FPLR, Non-Shielded
[5 empty] | DH98 | 0.00054 |  | 0 | 0 | [7 empty] | Paige 5U1802S3B1 | 18 | 0.0065 | 24 | 0.108 | Solid, FPLP, Non-Shielded |  |  | Paige 5U1802S3B1 | 18 | 0.0065 | 24 | 0.108 | Solid, FPLP, Non-Shielded | Solid, FPLP, Non-Shielded
Do not exceed the maximum wire length as recommended by this calculator. If you require additional information |  |  |  |  | DH98AR | 0.00054 |  | 0 | 0 | [7 empty] | Paige 454722ARE | 18 | 0.00639 | 64.8 | 0.059 | Solid, FPLR, Shielded |  |  | Paige 454722ARE | 18 | 0.00639 | 64.8 | 0.059 | Solid, FPLR, Shielded | Solid, FPLR, Shielded
please contact Hochiki America. |  |  |  |  | DH99A | 0.00054 |  | 0 | 0 | [7 empty] | Paige 454717ARER | 18 | 0.00639 | 49.3 | 0.067 | Solid, FPLP, Shielded |  |  | Paige 454717ARER | 18 | 0.00639 | 49.3 | 0.067 | Solid, FPLP, Shielded | Solid, FPLP, Shielded
[5 empty] | DH99AR | 0.00054 |  | 0 | 0 | [7 empty] | Paige 454731ARE | 16 | 0.00401 | 40.6 | 0.099 | Solid, FPLR, Non-Shielded |  |  | Paige 454731ARE | 16 | 0.00401 | 40.6 | 0.099 | Solid, FPLR, Non-Shielded | Solid, FPLR, Non-Shielded
[5 empty] | FRCME-4 | 0.00066 |  | 0 | 0 | [7 empty] | Paige 454740ARE | 16 | 0.00419 | 36 | 0.108 | Solid, FPLP, Non-Shielded |  |  | Paige 454740ARE | 16 | 0.00419 | 36 | 0.108 | Solid, FPLP, Non-Shielded | Solid, FPLP, Non-Shielded
[5 empty] | FRCMA | 0.00063 |  | 0 | 0 | //FRCMA/FRCMA-I use standby current in this calculation because alarm current includes LED | [6 empty] | Paige 4S1602S3B1 | 16 | 0.00401 | 72 | 0.052 | Solid, FPL, Shielded |  |  | Paige 4S1602S3B1 | 16 | 0.00401 | 72 | 0.052 | Solid, FPL, Shielded | Solid, FPL, Shielded
| Wire Information: |  |  |  | FRCMA-I | 0.00063 |  | 0 | 0 | [7 empty] | Paige 454736ARE | 16 | 0.0041 | 72 | 0.056 | Solid, FPLR, Shielded |  |  | Paige 454736ARE | 16 | 0.0041 | 72 | 0.056 | Solid, FPLR, Shielded | Solid, FPLR, Shielded
|  | SLC 1 | SLC 2 |  | FRCME-M | 0.00036 |  | 0 | 0 | [7 empty] | Paige 454747ARE | 16 | 0.00402 | 52.9 | 0.059 | Solid, FPLP, Shielded |  |  | Paige 454747ARE | 16 | 0.00402 | 52.9 | 0.059 | Solid, FPLP, Shielded | Solid, FPLP, Shielded
[5 empty] | DIMM | 0.00072 |  | 0 | 0 | [7 empty] | Paige 4U1402S3B1 | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPL, Non-Shielded |  |  | Paige 4U1402S3B1 | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPL, Non-Shielded | Solid, FPL, Non-Shielded
[5 empty] | AMS | 0.00066 |  | 0 | 0 | [7 empty] | Paige 454718ARE | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPLR, Non-Shielded |  |  | Paige 454718ARE | 14 | 0.00252 | 44.7 | 0.1 | Solid, FPLR, Non-Shielded | Solid, FPLR, Non-Shielded
| Edit Custom Wire Information: |  |  |  | CZM | 0.00072 |  | 0 | 0 | [7 empty] | Paige 5U1402S3R1 | 14 | 0.0025 | 27 | 0.103 | Solid, FPLP, Non-Shielded |  |  | Paige 5U1402S3R1 | 14 | 0.0025 | 27 | 0.103 | Solid, FPLP, Non-Shielded | Solid, FPLP, Non-Shielded
[5 empty] | SOM | 0.000161 |  | 0 | 0 | [7 empty] | Paige 4S1402S3R1 | 14 | 0.00252 | 58 | 0.052 | Solid, FPL, Shielded |  |  | Paige 4S1402S3R1 | 14 | 0.00252 | 58 | 0.052 | Solid, FPL, Shielded | Solid, FPL, Shielded
| Size: | 18 | 18 |  | SOM-A | 0.0005 |  | 0 | 0 | [7 empty] | Paige 454726ARE | 14 | 0.00252 | 58 | 0.052 | Solid, FPLR, Shielded |  |  | Paige 454726ARE | 14 | 0.00252 | 58 | 0.052 | Solid, FPLR, Shielded | Solid, FPLR, Shielded
| Resistance (Ω/ft): | 0.00639 | 0.00639 |  | SOM-AI | 0.0005 |  | 0 | 0 |  | SCI Calculation | R | SLC1 | SLC2 |  |  | Paige 454727ARE | 14 | 0.00253 | 67 | 0.053 | Solid, FPLP, Shielded |  |  | Paige 454727ARE | 14 | 0.00253 | 67 | 0.053 | Solid, FPLP, Shielded | Solid, FPLP, Shielded
| Capacitance (pF/ft): | 38.4 | 38.4 |  | SOM-R | 0.00016 |  | 0 | 0 |  | SCI Bases | 3e-05 | 0 | 0 | (row 59) |  | Custom | 18 | 0.00111 | 40.12 | 0.123 | Enter Description Here... |  |  | Custom | 18 | 0.00222 | 40.12 | 0.122 | Enter Description Here... | Enter Description Here
| Inductance (µH/ft): | 0.106 | 0.106 |  | R2M | 0.0004 |  | 0 | 0 |  | FRCMA-I | 3e-05 | 0 | 0 | (row 44)
|  | Solid, FPL, Non-Shielded | Solid, FPL, Non-Shielded |  | R2ML/H | 0.000405 |  | 0 | 0 |  | SOM-AI | 3e-05 | 0 | 0 | (row 52)
[5 empty] | R2ML/H-I | 0.000405 |  | 0 | 0 |  | R2M-I | 3e-05 | 0 | 0 | (row 57)
[5 empty] | SCI | 0.00027 |  | 0 | 0 |  | SCI | 5e-05 | 0 | 0 | (row 58)
|  | SLC 1 | SLC 2 |  | SCI_Base | 0.00016 |  | 0 | 0
| Number of Devices | 0 | 0 |  | ACC | 0.00054 |  | 0 | 0
[5 empty] | ASBL | 0.00015 |  | 0 | 0
| MAX SLC Wire Length | 0 | 0 | feet
[12 empty] | SCI Rtotal | 0 | 0
Overall Length Limited by:
// If any of the row numbers are changed on the battery calculator sheet this must be updated.
[7 empty] | Sub -> | 0 | 0
[5 empty] | 5 LEDs | 0.04 |  | 0 | 0
[5 empty] | Comms | 0.007 |  | 0 | 0
[7 empty] | Total -> | 0 | 0 | //worst-case maximum current for each SLC
For information on how to measure the total SLC wire length, click here: | [6 empty] | Rtotal | 0 | 0 | //this is the total maximum resistance for the SLC based on V/I
//V = 6 volt drop maximum for FireNET and FireNET Plus panels
|  | Paige Wire nominal OD (for conduit fill calculations) |  |  |  |  | SCI Rtotal | 0 | 0 | //this is the total resistance of SCI devices on the circuit.
|  | 18AWG | 16AWG | 14AWG
|  | 4U1802S3B1 - 0.161" | 454731ARE - 0.180" | 4U1402S3B1 - 0.220" |  |  | Wire Rmax | 0 | 0 | //adjusted total resistance after subtracting SCIs
|  | 454703ARE - 0.160" | 454740ARE - 0.170" | 454718ARE - 0.220" |  |  | Adjusted Rmax | 0 | 0 | //since the DCP spec states "less than 50 ohms" I set this to be 49.9 ohms maximum
|  | 5U1802S3B1 - 0.134" | 4S1602S3B1 - 0.161" | 5U1402S3R1 - 0.206"
|  | 454722ARE - 0.161" | 454736ARE - 0.160" | 4S1402S3R1 - 0.218"
|  | 454717ARER - 0.145" | 454747ARE - 0.170" | 454726ARE - 0.210"
|  |  |  | 454727ARE - 0.200" |  |  | CableResistance | 0.00639 | 0.00639
[7 empty] | MaxWire based on Resistance | 0 | 0 | //this is the maximum wire length based on the resistance, Rmax divided by the cable resistance per foot
[7 empty] | CableCapacitance | 38.4 | 38.4
[7 empty] | MaxWire based on Capacitance | 25781.25 | 25781.25 | //max capacitance = .99µf total (less than 1µf). This is used to determine max wire length based on capacitance. Note that pf is used for the calculation (.99µf = 990000pf)
NOTE: Hochiki hereby disclaims all warranties relating to this software product, whether expressed or implied, including
without limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki cannot and will not | [6 empty] | CableInductance | 0.106 | 0.106
be liable for any incidental, consequential, special, indirect or similar damages for any reason. It is the responsibility of the | [6 empty] | MaxWire based on Inductance | 9339.6226 | 9339.6226 | //max inductance = .99mH total (less than 1mH). This is used to determine max wire length based on inductance. Note that µH is used for the calculation (.99mH - 990µH)
user to ascertain the accuracy and the reliability of any and all information generated or provided by this software.
Revision | 3.056
[7 empty] | Maximum SLC Length | 0 | 0 | //determines and displays the max SLC length based on limiting factor (resistance, inductance, capacitance)
[8 empty] | 0 | 0 | //limits max SLC length to preset value
[7 empty] | SLC Preset Length Value (ft.) | 10000 |  | //this is the preset SLC length. This is the maximum distance that the calculator will display to the user. Change the number in this cell to adjust the maximum distance.
//Operation of wire selection tool
//drop down boxes are ActiveX combo boxes. The range displayed in the list is set in the properties for the controls.
//The linked cells for the combo boxes are at AM3:AM6.
[6 empty] | Class B |  |  |  | //AF2:AJ5 uses VLOOKUP to find the correct information for the wire that has been selected.
[6 empty] | Class B with T-taps |  |  |  | //The buttons call a user form. When the user form is closed, the data entered is written to the "Custom" row in each SLC's data table
[6 empty] | Class A |  |  |  | // The data in AF2:AJ5 is copied to the cells on the part of the form that is visible to the user
//To update the wire information:
//the information in the tables must be updated for all 4 SLCs
// the range may need to be changed for each combo box (if the number of table entries have changed)
//the range may need to be changed for the VLOOKUP formulas (if the number of table entries have changed)
//If the location of the "Custom" wire cells has changed, the VB code must be changed for the cmdAdd_click events
//(this event writes the user-entered information to specific cells on the sheet. cmdSaveAll_click on user form 1 must be changed too)
Note on C31: All addressable SLC devices. NOTE: this number may exceed 127 if ASB / ASBLs are used.
The maximum values for the SLC are:
Resistance - less than 50 ohms
Capacitance - less than 1 µF
Inductance - less than 1 mH
Description:
FireNET Plus SLC Wire Length Calculator